## 03A O&M Manual Req. OCM
Operations & Maintenance PPP/PFI Handback Requirements
Version |  | 1 | Date | Insert date
|  |  | >This Operations & Maintenance PPP/PFI handback work book is the default starting point for information required on asset and data transfer for facilities approaching handback. This table should be reviewed collaboratively between the parties (Project Co, Management Services Provider, FM Provider and the Authority) and refined (as required) as operational PPP projects commence their handback journey >The information deliverables, responsibilities and pre-handover requirements should be established via Columns C, D, L & M. Column "C" indicates information required under the Project Agreement with Column "D" used for any additional project information and or data. >Ideally, any necessary table adjustments should be in accordance with the Uniclass 2015 Project Management (PM) & System (Ss) table versions available at the handback inception stage. >This work book and supporting user guide is for guidance only as it sets a template baseline for expected data and handback information. Every project will have its own specific project asset and data handover requirements and authorities should consider this in detail and where appropriate, seek independent technical and or legal advice in this regard. | [7 empty] | Adopted Uniclass table versions: - Project Management (PM) - July 2023 - v1.21 Systems (Ss) - July 2023 - v1.31
|  |  | Required for handback | Sections headed in "Sky Blue" signifies information required that has either been generated during the operational period or is a specific requirement for handback.
|  |  | Info issued at PC/SC | Sections headed in "Yellow" signifies compliance and certification documentation or information generated during the development/construction period issued at practical completion and or prior to services commencement.
Row Number | Project Agreement Requirement | Additional Requirement | PM Code | (PM) Description | Handover/Handback information heading | Asset register ref | Information handover requirements | System (Ss) Code | Information Description | Resp lead party for information delivery | Information Delivery Status | Additional comments | Project Agreement Requirement | Additional Requirement | Resp lead party for information delivery | Information Delivery Status
<pick list> | <pick list> | <pick list> | [7 empty] | <pick list> | <pick list> |  | No | No | Project Co | TBC
1.01 |  |  |  | Key operational contract administration information required for handback (end of contract) |  |  | Copies of all key commercial, financial and legal documents related to the project or project facilities. | [5 empty] | Yes | Yes | Project Co TA | Not Issued
1.01 | Yes | Yes | PM_55_55 | Contract | Project Bible - the complete Project Agreement (PA) and PA related information including all schedules to the PA |  | To include all schedule i.e. FM service specification, payment mechanism, head and sub leases etc |  | The specific technical schedules/ details are covered in a separate section contained within this workbook | Project Co | TBC |  | Disputed | If Available | MSA Provider | Date Agreed
1.02 | No | No | PM_55_55 | Contract | Supplemental agreements |  | To include any agreed side agreements/letters and or other agreed commercial positions |  |  | Project Co TA | Not Issued |  |  | N/A | FM Contractor | Date Expired
1.03 | Disputed | If Available | PM_60_50 | Contract cost management | Financial models |  | Financial close model including any updated operational financial models |  |  | MSA Provider | Date Agreed |  |  |  | Under Review PrjCo | Closed
1.04 |  | N/A | PM_60_60_15 | Contract contacts list | Key project contact list - all stakeholders |  | To include key authority sponsors, Project Co and project related parties contact details |  |  | FM Contractor | Date Expired |  |  |  | TBC
1.05 |  |  | PM_50_30_12 | Commercial compliance report | Annual operational contract management/performance reports |  | Performance reports issued by Project Co to the authority - min requirement last 10 years |  | [Minimum last 10 years reports] | Under Review PrjCo | Closed |  |  |  | Authority
1.06 |  |  | PM_35_70 | Energy performance requirements | Historical energy, carbon and utilities information |  | To include energy reports, historical consumption data - agree what information will be required and in what format |  | [Minimum last 10 years reports] | TBC
1.07 |  |  | PM_10_20_14 | Community and tenant liaison plan | Community use and third party let information. |  | Include key contract information, process and charging arrangement where applicable |  |  | Authority
1.08 |  |  | PM_30_10 | Site survey information | Historical/previous building/asset condition surveys. |  | In addition to any asset condition survey information, include any handback surveys |  | Clarity required around the format of this information
1.09 |  |  | PM_30_10 | Site survey information | Record of building development and replacement works. |  | Typically where there have been extensions to the facilities or temporary accommodation installed on site
1.1 |  |  | PM_40_60_22 | Data security policy | Records of all freedom of information requests.
1.11 |  |  | PM_40_60_27 | Electronic data interchange (EDI) | Help desk information |  | Agree what information will be required and in what format |  | [Minimum last 5 years reports]
1.12 |  |  | PM_40_60_27 | Electronic data interchange (EDI) | Help desk software licence information
1.13 |  |  | PM_80_20_19 | Contacts list | Third party contact information |  | Typically suppliers, specialist providers
1.14 |  |  | PM_80_30_80 | Staff cost information | TUPE Information. |  | This information includes, for example, the identity and age of those employees, written particulars of employment information (under section 1 of the Employment Rights Act 1996) and details of any tribunal claims that the transferor reasonably believes might be brought. |  | Consider if this information should included in a project specific TUPE transfer plan.
1.15 |  |  | PM_60_50_23 | Cost estimate | Legacy Variation/Change procedure information |  | All information relating to contract variations or contract changes. Information should include the impact both in terms of cost, maintenance and lifecycle maintenance |  | Ideally the information should include associated costs and commercial position i.e. any FM or LCM implications
1.16 |  |  | PM_80_60 | Asset risk management information | Project Risk Registers - Project level |  | Operational period risk registers
1.17 |  |  |  | < add new row for each additional deliverable>
2 |  |  | PM_70_15 | Compliance and certification documents | Compliance and certification documents issued at practical completion/services commencement |  | Copies of all listed compliance and certification documents for any maintainable systems / product assets installed in the building at the point of construction handover. |  | This is typically the information handed over at construction competition.
2.01 |  |  | PM_70_15_07 | Building control completion certificate | Building control completion certificates
2.02 |  |  | PM_70_15_08 | Building control occupation certificate | Building control occupation certificates
2.03 |  |  | PM_70_15_13 | Chlorination certificate | Chlorination certificates |  |  | Ss_55_15 | Water extraction, treatment and storage systems
2.04 |  |  | PM_70_15_25 | Emergency lighting certificate | Emergency lighting certificates |  |  | Ss_70_80_33 | General space lighting systems
2.05 |  |  | PM_70_15_27 | Electrical test certificate | Electricity - Fixed electrical testing and certification |  | Copies of all relevant Electrical Safety Certificates and fixed electrical testing certificates | Ss_70_30 | Electricity distribution systems
2.06 |  |  | PM_70_15_28 | Fire alarm electrical supply test certificate | Fire alarm electrical supply test certificates |  |  | Ss_75_50_28 | Fire and smoke detection and alarm systems
2.07 |  |  | PM_70_15_29 | Fire safety acceptance certificate | Fire safety acceptance certificates |  |  | Ss_75_50_28 | Fire and smoke detection and alarm systems
2.08 |  |  | PM_70_15_30 | Fire-stopping protection certificate | Fire-stopping protection certificates |  |  | Ss_25_60_30 | Fire-stopping systems
2.09 |  |  | PM_70_15_31 | Fire-stopping protection register | Fire-stopping protection registers |  |  | Ss_25_60_30 | Fire-stopping systems
2.1 |  |  | PM_70_15_34 | Gas installation safety certificate | Gas installation safety certificates |  |  | Ss_55_20_33 | Gas distribution network systems
2.11 |  |  | PM_70_15_40 | Incoming gas supply pressure test reports | Incoming gas supply pressure test reports |  |  | Ss_55_20_34 | Gas supply systems
2.12 |  |  | PM_70_15_42 | Insurance certificate | Insurance certificates
2.13 |  |  | PM_70_15_63 | Power metering commissioning certificate | Power metering commissioning certificates |  |  | Ss_75_70_54 | Metering, monitoring and management systems
2.14 |  |  | PM_70_15_65 | Primary fresh air supply test certificate | Primary fresh air supply test certificates |  |  | Ss_65_40_33 | General space ventilation systems
2.15 |  |  | PM_70_15_76 | Secondary and backup electricity supplies test certificate | Secondary and backup electricity supplies test certificates |  |  | Ss_70_30 | Electricity distribution systems
2.16 |  |  | PM_70_15_80 | Smoke and fire alarm and fire suppression system telephone lines test results | Smoke and fire alarm and fire suppression system telephone lines test results |  |  | Ss_75_50_28 | Fire and smoke detection and alarm systems
2.17 |  |  | PM_70_15_82 | Soak test results | Soak test results
2.18 |  |  | PM_70_15_84 | Structured data cabling test certificate | Structured data and telephone systems cabling test certificates |  |  | Ss_75_10_21 | Data distribution and telecommunications systems
2.19 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water quality and flushing test certificates |  |  | Ss_55_15 | Water extraction, treatment and storage systems
2.2 |  |  | PM_70_80_79 | Smoke extract and control system commissioning certificate | Smoke extract and control system commissioning & test certificates |  |  | Ss_65_40_80 | Smoke extract and control systems
2.21 |  |  |  | < add new row for each additional deliverable>
3 |  |  | PM_70_30 | Equipment certification documents | Equipment certification documents issued at practical completion/services commencement |  | Copies of all equipment certification for any maintainable systems / product assets installed in the building. |  | This is typically the information handed over at construction competition.
3.01 |  |  | PM_70_30_02 | Air handling unit commissioning certificate | Air handling unit commissioning certificate |  |  | Ss_65 | Ventilation and air conditioning systems
3.02 |  |  | PM_70_30_06 | Boiler commissioning certificate | Boiler commissioning certificate |  |  | Ss_60_40_37 | Heating systems. This should also include steam boilers and required certification
3.03 |  |  | PM_70_30_10 | Building management systems (BMS) commissioning certificate | Building management systems (BMS) commissioning certificate |  |  | Ss_75_70 | Control and management systems
3.04 |  |  | PM_70_30_15 | Closed-circuit television (CCTV) commissioning certificate | Closed-circuit television (CCTV) commissioning certificate |  |  | Ss_75_40_53_86 | Surveillance CCTV systems
3.05 |  |  | PM_70_30_22 | Disabled alarms and disabled refuge alarm testing certificate | Disabled alarms and disabled refuge alarm testing certificate |  |  | Ss_75_50_11 | Emergency call systems
3.06 |  |  | PM_70_30_26 | Equipment safety certificate | Equipment safety certificate |  |  | Ss_75_50 | Safety and protection systems
3.07 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire hydrant and mains commissioning certificate |  |  | Ss_55_30_96 | Water firefighting systems
3.08 |  |  | PM_70_30_28 | Fire-rated doors test certificate | Fire-rated doors test certificate |  |  | Ss_25_30_20_25 | Door set systems
3.09 |  |  | PM_70_30_47 | Lightning protection certificate | Lightning protection certificate |  |  | Ss_70_30_25_45 | Lightning protection systems
3.1 |  |  | PM_70_30_78 | Security and intruder alarm commissioning certificate | Security and intruder alarm commissioning certificate |  |  | Ss_75_40_75 | Security detection alarm systems
3.11 |  |  | PM_70_30_83 | Sprinkler installation test certificate | Sprinkler installation test certificate |  |  | Ss_55_30_98_85 | Sprinkler systems
3.12 |  |  | PM_70_30_97 | Window certificates | Window certificates |  |  | Ss_25_30_95_95 | Window systems
3.13 |  |  | PM_70_30_92 | Uninterruptible power supply (UPS) test certificate | Uninterruptible power supply (UPS) test certificate |  |  | Ss_70_30_45_92 | Uninterruptible power supply systems
3.14 |  |  |  | < add new row for each additional deliverable>
4 |  |  | PM_70_75 | Testing information | Testing information issued at practical completion/services commencement |  | Copies of all testing information for any maintainable systems / product assets installed in the building. |  | This is typically the information handed over at construction competition.
4.01 |  |  | PM_70_75_08 | Boiler test report | Boiler test reports |  |  | Ss_60_40_37 | Heating systems
4.02 |  |  | PM_70_75_10 | Chlorination test report | Chlorination test reports |  |  | Ss_55_15 | Water extraction, treatment and storage systems
4.03 |  |  | PM_70_75_15 | Control system test report | Control system test reports |  |  | Ss_75_70 | Control and management systems
4.04 |  |  | PM_70_75_21 | Disabled alarms and disabled refuge alarm test report | Disabled alarms and disabled refuge alarm test reports |  |  | Ss_75_50 | Safety and protection systems
4.05 |  |  | PM_70_75_22 | Drainage leakage test results | Drainage leakage test results |  |  | Ss_50 | Disposal systems
4.06 |  |  | PM_70_75_23 | Ductwork cleaning test certificate | Ductwork cleaning test certificate |  |  | Ss_65_40 | Ventilation systems
4.07 |  |  | PM_70_75_25 | Ductwork pressure test certificate | Ductwork pressure test certificate |  |  | Ss_65_40 | Ventilation systems to include volume flow rates
4.08 |  |  | PM_70_75_27 | Electrical installation test report | Electrical installation test report |  |  | Ss_70_30 | Electricity distribution systems
4.09 |  |  | PM_70_75_28 | Emergency lighting test report | Emergency lighting test report |  |  | Ss_70_30_25 | Electrical protection systems
4.1 |  |  | PM_70_75_30 | Fire protection installation test report | Fire protection installation test report |  |  | Ss_75_50 | Safety and protection systems
4.11 |  |  | PM_70_75_31 | Fire alarm test certificate | Fire alarm test certificate |  |  | Ss_75_50 | Safety and protection systems
4.12 |  |  | PM_70_75_36 | Heating installation test report | Heating installation test report |  |  | Ss_60_40_37 | Heating systems
4.13 |  |  | PM_70_75_37 | High-voltage electrical installation test report | High-voltage electrical installation test report |  |  | Ss_70_30 | Electricity distribution systems
4.14 |  |  | PM_70_75_40 | Information and communications technology (ICT) infrastructure test report | Information and communications technology (ICT) infrastructure test report |  |  | Ss_75_10 | Communications systems
4.15 |  |  | PM_70_75_47 | Lifts test report | Lifts test report |  |  | Ss_80_50 | Lift systems
4.16 |  |  | PM_70_75_48 | Lighting lux level test report | Lighting lux level test report |  |  | Ss_70_80 | Lighting systems
4.17 |  |  | PM_70_75_49 | Lightning protection installation test report | Lightning protection installation test report |  |  | Ss_70_30_25_45 | Lightning protection systems
4.18 |  |  | PM_70_75_63 | Pipeline pressure test certificate | Pipeline pressure test certificate |  |  | Ss_55 | Piped supply systems
4.19 |  |  | PM_70_75_65 | Pressure system installation test report | Pressure system installation test report |  |  | Ss_55 | Piped supply systems
4.2 |  |  | PM_70_75_68 | Public health installation test report | Public health installation test report |  |  | Ss_55_70 | Water distribution and supply systems
4.21 |  |  | PM_70_75_83 | Sound and lighting systems test report | Sound and lighting systems test report |  |  | Ss_70_80 | Lighting systems
4.22 |  |  | PM_70_75_85 | Surveillance equipment installation test report | Surveillance equipment installation test report |  |  | Ss_75_40_53 | Monitoring systems
4.23 |  |  | PM_70_75_88 | Telecommunications installation test report | Telecommunications installation test report |  |  | Ss_75_10_21_88 | Telecommunications systems
4.24 |  |  | PM_70_75_94 | Ventilation test report | Ventilation test report |  |  | Ss_65_40 | Ventilation systems
4.25 |  |  | PM_70_75_96 | Water distribution pressure test report | Water distribution pressure test report |  |  | Ss_55_70 | Water distribution and supply systems
4.26 |  |  |  | < add new row for each additional deliverable>
5 |  |  | PM_70_80 | Commissioning information | Commissioning information issued at practical completion/services commencement |  | Record and copies of all commissioning reports and certificates for any maintainable systems / assets installed in the building. Min. information to include: •plant information (model, type) •measurement information and points •used test equipment •details of calibration certificates •For handover, a statement of whether design requirements were achieved. |  | This is typically the information handed over at construction competition.
5.01 |  |  | PM_70_80_01 | Access control commissioning certificate | Access control commissioning certificate |  |  | plant information (model, type) | Access control systems
5.02 |  |  | PM_70_80_02 | Air distribution systems commissioning report | Air distribution systems commissioning report |  |  | measurement information and points | Ventilation and air conditioning systems
5.03 |  |  | PM_70_80_03 | Air conditioning systems commissioning certificate | Air conditioning systems commissioning certificate |  |  | used test equipment | Ventilation and air conditioning systems
5.04 |  |  | PM_70_80_05 | Audio-visual systems commissioning and acceptance certificate | Audio-visual systems commissioning and acceptance certificate |  |  | details of calibration certificates | Communications systems
5.05 |  |  | PM_70_80_14 | Communications systems commissioning certificate | Communications systems commissioning certificate |  |  | For handover, a statement of whether design requirements were achieved. | Communications systems
5.06 |  |  | PM_70_80_15 | Control system commissioning report | Control system commissioning report |  |  | Ss_75_70 | Control and management systems
5.07 |  |  | PM_70_80_28 | Emergency lighting installation commissioning report | Emergency lighting installation commissioning report |  |  | Ss_70_30_25 | Electrical protection systems
5.08 |  |  | PM_70_80_30 | Fire alarm system commissioning certificate | Fire alarm system commissioning certificate |  |  | Ss_75_50 | Safety and protection systems
5.09 |  |  | PM_70_80_31 | Fire suppression system commissioning certificate | Fire suppression system commissioning certificate |  |  | Ss_55_30 | Fire-extinguishing systems
5.1 |  |  | PM_70_80_42 | Induction loop commissioning certificate | Induction loop commissioning certificate |  |  | Ss_75_10_46 | Listening systems
5.11 |  |  | PM_70_80_46 | Lifts commissioning certificate | Lifts commissioning certificate |  |  | Ss_80_50 | Lift systems
5.12 |  |  | PM_70_80_47 | Lifts commissioning report | Lifts commissioning report |  |  | Ss_80_50 | Lift systems
5.13 |  |  | PM_70_80_48 | Lighting commissioning report | Lighting commissioning report |  |  | Ss_70_80 | Lighting systems
5.14 |  |  | PM_70_80_49 | Lighting control certificate | Lighting control certificate |  |  | Ss_70_80 | Lighting systems
5.15 |  |  | PM_70_80_77 | Security system commissioning report | Security system commissioning report |  |  | Ss_75_40 | Security systems
5.16 |  |  | PM_70_80_80 | Smoke extract and control system commissioning report | Smoke extract and control system commissioning report |  |  | Ss_65_40_80 | Smoke extract and control systems
5.17 |  |  | PM_70_80_85 | Surveillance system installation commissioning report | Surveillance system installation commissioning report |  |  | Ss_75_40_53 | Monitoring systems
5.18 |  |  | PM_70_80_89 | Toilet alarm commissioning certificate | Toilet alarm commissioning certificate |  |  | Ss_75_50_11 | Emergency call systems
5.19 |  |  | PM_70_80_94 | Ventilation commissioning certificate | Ventilation commissioning certificate |  |  | Ss_65_40 | Ventilation systems
5.2 |  |  | PM_70_80_96 | Water distribution commissioning report | Water distribution commissioning report |  |  | Ss_55_70 | Water distribution and supply systems
5.21 |  |  |  | < add new row for each additional deliverable>
6 |  |  | PM_70_85 | Completion information | Completion information issued at practical completion/services commencement |  | Copies of all completion information relative to the building handover process and installed maintainable systems and associated products/ assets.
6.01 |  |  | PM_70_85_10 | Building manual | Building manual |  | Refer to BSRIA 26 building manual as suggested baseline template. Min. information to include : building identifier details, general contact details, Building and floor plan layouts, An overview of the buildings design intent & construction principles. A summary of each installed system. min. to include: • design/ condition parameters • services required to operate • intended method of control
6.02 |  |  | PM_70_85_25 | End user operating information: | End user operating information: |  | Recommended strategy for operation and control of each engineering system and associated assets inc. an outline of the general operating mode. To include: • both normal and emergency conditions • target figures for energy consumption and energy costs
6.03 |  |  | PM_70_85_25_01 | Control | Control |  | Control information (requirements & records for up to handover) min. to include asset: • location • effect •object • sequence • limits of capability • modes • set points. . Interlocks information between different plants inc. • cause and effect details for each. NB: The project COBie data deliverable may provide part of the above information.
6.04 |  |  | PM_70_85_25_02 | Lubrication | Lubrication |  | A schedule of plant requiring lubrication. Min. information to include: • manufacturers recommendations on lubrication types • any British Standard references • method of frequency and application • any product related special storage and handling requirements.
6.05 |  |  | PM_70_85_25_03 | Modifications | Modifications |  | A record of permitted modifications allowed by manufacturers and/ or system designers for installed plant and/or systems. Provide a blank log for recording future modifications and changes as they occur, including a recommended QA procedure for upkeep in the operational phase.
6.06 |  |  | PM_70_85_25_04 | Disposal | Disposal |  | A record of disposal instructions particularly in relation to known hazards or dangers. Min. to include: • Any known dangers likely to arise during the disposal of specific items of plant or equipment, together with the necessary precautions and safety measures • Methods for safely disposing of or destroying the equipment or parts thereof, including packaging, insulation and fluids • Links to sources from which further advice can be obtained • Recycling information for the specific item of plant.
6.07 |  |  | PM_70_85_30 | Final inspection report | Final inspection report
6.08 |  |  | PM_70_85_40 | Health and safety file | Health and safety file |  | To include but not limited to : certificates, hazard & safety precautions statement. O&M safety information in relation to working access, working zones, future plant removal, safe operating procedures (SOP & EOP), and the means by which potentially hazardous plant can be made safe.
6.09 |  |  | PM_70_85_45 | List of spares and consumables | List of spares and consumables |  | A Spares policy including recommended and handover stock levels. A parts identification list. min. to include: • details of replaceable assemblies, sub-assemblies and components based on manufacturers/ suppliers recommendations for spares & running spares. • details of local stockists where applicable. |  | This should included critical spares schedule utilised thought the operational period.
6.1 |  |  | PM_70_85_50 | Maintenance schedules | Maintenance schedules |  | Maintenance schedules for all preventative maintenance tasks, based on manufacturers recommendations or other statutory or mandatory requirements. Task frequencies to be included. Additional information may include details on required: • Inspections • Examinations • Tests • Adjustments • Calibration • Lubrication • Periodic overhaul.
6.11 |  |  | PM_70_85_52 | Manufacturer information | Manufacturer information |  | A complete set of manufacturers literature and information for maintainable assets, plant and equipment installed and assembled within the building and services systems. Individual literature content should be provided for each installed asset type (i.e., full library catalogues or grouped .pdf documentation for a range of different asset types is not permitted). Each document should be named in accordance with the project defined document naming and asset naming / code conventions, in full alignment with the final asset register. As a min. the handover should include, where relevant: • Description of the product as purchased • The date of purchase • Performance / behavioural characteristics of the equipment in use • Applications (suitability for use) • Operation and maintenance details •Labour, plant, materials and spatial resources required • Methods of operation and control (covered by PM_70_85_25 and PM_70_85_55) • Cleaning and maintenance requirements • Protective measures • Labour safety and welfare associated with the equipment • Public safety considerations. NB: The project COBie data deliverable may provide part of the above information.
6.12 |  |  | PM_70_85_55 | Operating instruction | Operating instruction |  | Standard operating (SOP) and emergency operating procedures (EOP) inc. standby plant. Min. to include: • start-up sequences • running and shut-down under normal and emergency conditions. • Provide photographs and/ or video (TBC) recordings of SOP's & EOP's. Record of procedures for the logical diagnosis and correction of faults. NB: Linked to health & safety.
6.13 |  |  | PM_70_85_60 | Plant logbook | Plant logbooks |  | A log for recording plant operations. min. to include: •plant running hours •energy consumption energy costs.
6.14 |  |  | PM_70_85_83 | Supplier directory | Supplier directory |  | A record of delivery team details (designers, contractor, supply chain) all manufacturers and suppliers. Min. data to include: • name • address • e-mail addresses of the appropriate contacts • address • telephone number • website in alphabetical order of name. NB: The project COBie data deliverable may provide part of the above information.
6.15 |  |  | PM_70_85_90 | Training documentation | Training documentation |  | Refer to SOP and EOP operating instruction delivery requirements • photographs and/ or video (TBC) recordings. A list of required pre-handover operator and user training / demonstrations should be provided by the client to the contractor at tender stage. |  |  |  |  | Training requirements for each applicable system to be specified by client at the project outset
6.16 |  |  | PM_70_85_93 | Utilities readings | Utilities readings
6.17 |  |  | PM_70_85_96 | Works completion certificate | Works completion certificate
6.18 |  |  | Currently not listed | Building User Guide | Building User Guide |  | Refer to BSRIA 26 building user guide for a suggested baseline template.
6.19 |  |  |  | Complete facility key register | Complete facility key register & door access systems |  |  |  | As well as keys, consideration should be given to access cards, access codes and other access devices, that provide access to all relevant areas of the Facilities, complete with all relevant schedules, i.e. suiting schedules etc.
6.2 |  |  |  | < add new row for each additional deliverable>
7 |  |  | PM_70_90 | Record information | Record information required for handback (end of contract) |  | A directory of information providing an as-constructed / as-fitted record of the building asset at handover. The record information will be delivered by all relevant parties (including product suppliers and site installers) and as a minimum include : • layout drawings • system schematics • production drawings • schedules • 3D models • Asset data (COBie) • Room data sheets • A master document register compiled from individual party document registers shall be delivered. A detailed description of each installed system shall be provided and as a minimum include: • system type • location and what it serves • dependencies • design related calculations and data • parameters & assumptions made during design process. • selection choice reasons • expected service life • planned operational efficiency. Each document should be named in accordance with the project defined document naming and asset naming / code conventions, in full alignment with the final asset register.
7.01 |  |  | PM_55_55 | Contract | Schedule of accommodation |  |  |  | Typically included as a separate file/CD to the project agreement bible - this should be validated
7.02 |  |  | PM_55_55 | Contract | Room data sheets |  |  |  | Typically included as a separate file/CD to the project agreement bible - this should be validated
7.03 |  |  | PM_55_55 | Contract | Authority construction requirements and contractors proposals. |  |  |  | Typically included as a separate file/CD to the project agreement bible - this should be validated
7.04 |  |  | PM_70_90_04 | Architectural record drawings | Architectural record drawings |  | Drawings to include any building development and replacement works. |  | Updated drawings to reflect any formal changes or alteration - applies to all record drawings.
7.05 |  |  | PM_70_90_15 | Control system record drawings | Control system record drawings
7.06 |  |  | PM_70_90_27 | Electrical systems record drawings | Electrical systems record drawings
7.07 |  |  | PM_70_90_30 | Fire system record drawings | Fire system record drawings
7.08 |  |  | PM_70_90_46 | Landscape record drawings | Landscape record drawings
7.09 |  |  | PM_70_90_52 | Mechanical systems record drawings | Mechanical systems record drawings
7.1 |  |  | PM_70_90_68 | Public health system record drawings | Public health system record drawings
7.11 |  |  | PM_70_90_77 | Security system record drawings | Security system record drawings
7.12 |  |  | PM_70_90_79 | Setting out records | Setting out records
7.13 |  |  | PM_70_90_83 | Structural record drawings | Structural record drawings
7.14 |  |  |  | < add new row for each additional deliverable>
8 |  |  | PM_80_10 | Asset strategy, planning and management information | Asset strategy, planning and management information required for handback (end of contract) |  | A record of all asset information required for operational management.
8.01 |  |  | PM_80_10_05 | Asset guarantee and warranty information | Asset guarantee and warranty information |  | Record of all relevant manufacture's guarantees & warranties inc. start dates, expiry dates & relevant contact details
8.02 |  |  | PM_80_10_10 | Asset register | Asset register |  | Refer to SFT template and associated guidance. Each individual asset (product) to have its own assigned asset code and corresponding site tag, verified with a photographic record of fixed installation on site. |  | To include all assets relating to the project. Ideally this should include a matrix of who own and is responsible for what. This is particularly import for health projects where Project Co may for example only be responsible for maintenance and not lifecycle replacement.
8.03 |  |  | PM_80_10_10 | Asset register | Equipment lists not included on asset register |  | Typically any office requirement, reprographic and or small intangible items of equipment
8.04 |  |  | PM_80_10_10 | Asset register | Catering and vending equipment if not included on asset register |  | Typically equipment provided by the catering provider
8.05 |  |  | PM_80_10_10 | Asset register | Cleaning and waste management equipment list |  | Typically equipment provided by the cleaning waste management service provider
8.06 |  |  | PM_80_10_10 | Asset register | External and landscaping equipment list |  | Typically equipment provided by the landscaping service provider - grounds maintenance and pitch maintenance equipment
8.07 |  |  | PM_80_10_10 | Asset register | Security and janitorial equipment list |  | Typically equipment required by janitorial staff - radio and communication equipment
8.08 |  |  | PM_80_10_10 | Asset register | Transferable consumables list |  | Typically cleaning, toilet and other related consumables
8.09 |  |  | PM_80_10_10 | Asset register | Transferable FM office equipment list |  | Management team office equipment
8.1 |  |  | PM_80_10_10 | Asset register | ICT Equipment |  | Helpdesk equipment, Building managements system front end and other service related ICT equipment including printers etc.
8.11 |  |  | PM_80_10_10 | Asset register | Intangible assets. |  | Typically asset that lacks physical substance - copyright, franchises, goodwill, trademarks, and trade names, as well as software.
8.12 |  |  | PM_80_10_47 | Loose equipment protocol | Loose fittings furniture and equipment (LFF&E) |  |  |  | The protocol should consider the process for how all LFF&E should be managed both in terms of identification and translon as part of handback
8.13 |  |  | PM_80_10_27 | Equipment schedule | Loose fittings furniture and equipment |  | To include all assets relating to the project. Ideally this should include a matrix of who own and is responsible for what. This is particularly import for health projects where Project Co may for example only be responsible for maintenance and not lifecycle replacement.
8.14 |  |  | PM_80_10_14 | Closed-circuit television (CCTV) strategy | Closed-circuit television (CCTV) strategy |  |  | Ss_75_40_53_86 | Surveillance CCTV systems
8.15 |  |  | PM_70_30_40 | Information and communications technology (ICT) security certification information | Information and communications technology (ICT) - software and system codes |  | information to allow access to ICT related project equipment, including HVAC, BMS, Fire and security systems. |  | Pin codes, access codes and passwords for access to systems etc.
8.16 |  |  | PM_80_10_22 | Display energy certificate | Display energy certificate
8.17 |  |  | PM_80_10_25 | Energy performance certificate | Energy performance certificate
8.18 |  |  | PM_80_10_24 | Energy consumption information | Records of utilities consumption |  |  |  | This should be considered in the context of the project agreement, particularly around any cap and collar and reporting requirements.
8.19 |  |  | PM_80_10_50 | Maintenance requirements | Maintenance requirements ( planned preventative maintenance) |  | Maintenance recommendations and instruction details for each item of plant and equipment installed. min. instruction information to include: • The isolation and return to service of plant and equipment • Adjustments, calibration and testing • Dismantling and re-assembly • The exchange of components and assemblies • Dealing with hazards that may arise during maintenance • The nature of deterioration and checks for defects • Special tools, test equipment and ancillary services • Decommissioning and end of life disposal.
8.2 |  |  | PM_80_10_55 | Metering strategy | Metering strategy |  | Include any sub metering and locations.
8.21 |  |  |  | < add new row for each additional deliverable>
9 |  |  | PM_80_15 | Asset maintenance information | Asset maintenance information required for handback (end of contract) |  | Copies of all information required for specific asset maintenance
9.01 |  |  | PM_80_15_31 | Fire safety log book | Fire safety log book
9.02 |  |  |  | < add new row for each additional deliverable>
10 |  |  | PM_80_30 | Asset life cycle cost information | Asset life cycle cost information for handback (end of contract) |  | A directory of cost data and information required for lifecycle operational management.
10.01 |  |  | PM_80_30_50 | Maintenance and repair cost information | Updated lifecycle maintenance model - funds already spent, allocated and planned. |  | Ideally an updated FC lifecycle model tracking spend and surpluses.
10.02 |  |  | PM_80_30_51 | Maintenance and lease agreement information | Lifecycle and maintenance plans. |  | Planned Lifecyle replacement to contract end
10.03 |  |  | PM_80_30_51 | Maintenance and lease agreement information | Lifecycle replacement records. |  | Records of all key Lifecyle replacement carried our to date
10.04 |  |  |  | < add new row for each additional deliverable>
11 |  |  | PM_80_50 | Emergency strategy information | Emergency strategy information for handback (end of contract) |  | Copies of all information required for emergency strategy planning, recovery and event response purposes.
11.01 |  |  | PM_80_50_25 | Disaster response strategy | Disaster response strategy |  | Information and site/ plan layouts on locations of essential utilities and emergency equipment. Record of contact details required in the event of an e.g. emergency, system failure or leak. examples but not limited to include: • utilities stop valves • isolators • fire hydrants • rising mains • extinguishers.
11.02 |  |  | PM_80_50_30 | Fire evacuation strategy | Fire evacuation strategy |  | fire strategy layouts and associated information
11.03 |  |  | PM_80_50_80 | Security strategy | Security strategy |  | security strategy layouts and associated information
11.04 |  |  | PM_80_50_27 | Emergency response packs | Emergency response packs
11.05 |  |  |  | < add new row for each additional deliverable>
12 |  |  | PM_80_60 | Asset risk management information | Asset risk management information for handback at end of contract |  | A directory of risk management information used for effective operational planning and management.
12.01 |  |  | PM_60_60_40 | Insurance policies and records | Health and safety - Employers Liability Insurance |  | Employers’ Liability (Compulsory Insurance) Regulations 1998 as amended |  | Copy of information
12.02 |  |  | PM_40_20_36 | Health and safety strategy | HSE poster |  | Health and Safety Information for Employees Regulations (HSIER) |  | Copy of information
12.03 |  |  | PM_70_85_40 | Health and safety file | Health and safety - Permit to work system |  | Copies of documented risk assessment system and legacy risk assessments • Control of Substances Hazardous to Health (COSHH) Regs 2002 • Confined Space Regulations 1997 Control of Asbestos at Work 2012 • Management of Health and Safety at Work Regulations • HS G 250 Guidance on Permit to Work Systems. • HS G 253 ‘The Safe Isolation of Plant and Equipment’.
12.04 |  |  | PM_60_70_70 | Site risk assessment | Health and safety - Risk assessments - HSWA 1974 The Management of Health and Safety at Work Regulations 1999 |  | Copies of documented risk assessment system and legacy risk assessments • Control of Substances Hazardous to Health Regulations 2002 (COSHH) • Control of Noise at Work Regulations 2005 • Manual Handling Operations Regulations 1992 • Health and Safety (Display Screen Equipment) Regulations 1992 • Personal Protective Equipment at Work Regulations 1992 • Regulatory Reform (Fire Safety) Order 2005 • Control of Asbestos Regulations 2012 • Dangerous Substances and Explosive Atmospheres Regulations 2002 • Work at Height Regulations 2005
12.05 |  |  | PM_80_10_01 | Asbestos management plan | Asbestos - Documentation - "Asbestos Risk Register" |  | Copies of all relevant documentation "Asbestos Risk Register" |  | Control of Asbestos Regulations 2012
12.06 |  |  | PM_30_40_06 | Asbestos survey report | Asbestos - Plans & risk assessments |  | Copies of all relevant documentation of all asbestos risk assessments |  | Control of Asbestos Regulations 2012
12.07 |  |  | PM_60_70_70 | Site risk assessment | Confined spaces - Documentation -"Confined Spaces Risk Register" |  | Copies of all relevant documentation "Confined Spaces Risk Register" |  | Confined Spaces Regulations 1997 ACOP L101
12.08 |  |  | PM_60_70_70 | Site risk assessment | Confined spaces - Plans & risk assessments |  | Copies of all relevant confined spaces risk assessments |  | Confined Spaces Regulations 1997 ACOP L101
12.09 |  |  | PM_60_70_70 | Site risk assessment | Confined spaces - Training records for relevant staff |  | Copies of all relevant training records for relevant staff |  | Confined Spaces Regulations 1997 ACOP L101
12.1 |  |  | PM_80_30_96 | Written scheme of examination information | Boilers and pressure vessels - Documentation - Copies written Scheme of Examination for all known Boilers and Pressure Systems |  | Copy of the updated current written Scheme of Examination for all known Boilers and Pressure Systems, and has it been approved by a “Competent Person”? |  | Pressure Systems Safety Regulations 2000 and ACOP L122
12.11 |  |  | PM_70_75_08 | Boiler test report | Boilers and pressure vessels - Inspection Records - Copies of all Boilers and Pressure Systems inspected. |  | Copies of all relevant boiler and pressure system inspections |  | Pressure Systems Safety Regulations 2000 and ACOP L122
12.12 |  |  | PM_70_75_97 | Window cleaning equipment test report | Window cleaning equipment
12.13 |  |  | PM_70_75_47 | Lifts test report | Lifting Equipment - Identification |  | Copies of all relevant lifting equipment register covering all assets covered by LOLER |  | LOLER 1998
12.14 |  |  | PM_70_75_47 | Lifts test report | Lifting Equipment - Inspection |  | Copies of all relevant inspection records/information for all passenger lifts and work platforms |  | LOLER 1998 |  |  | Includes all passenger lifts, goods lifts and mobile elevating work platforms (MEWP’s) inspected at least 6-monthly by a Competent Person?
12.15 |  |  | PM_70_75_47 | Lifts test report | Lifting Equipment - Inspection |  | Copies of all relevant inspection records/information for all other lifting equipment |  | LOLER 1998
12.16 |  |  | PM_70_75_47 | Lifts test report | Lifting Equipment - Documentation |  | Copy of the relevant written Scheme of Examination for all lifting equipment |  | LOLER 1998
12.17 |  |  | PM_70_75_47 | Lifts test report | Lifting Equipment - Escalators |  | Copies of all relevant inspection records/information for all escalators |  | LOLER/PUWER Regulations 1998
12.18 |  |  | PM_80_60_31 | Fire risk assessment information | Fire safety - Plans & risk assessments |  | Copies of all relevant Emergency and Escape Plans |  | The Regulatory Reform (Fire Safety) Order 2005
12.19 |  |  | PM_80_15_31 | Fire safety log book | Fire safety - Equipment |  | Copy of the firefighting appliances register |  | The Regulatory Reform (Fire Safety) Order 2005 |  |  | Copy of Is there a sufficient number of suitable firefighting appliances (rule of thumb is one extinguisher for every 200 sq.m. of floor space)?
12.2 |  |  | PM_80_15_31 | Fire safety log book | Fire safety - Fire alarm testing |  | Copies of all relevant fire alarm testing records |  | BS5839 including records of sounder and audibility tests
12.21 |  |  | PM_80_15_31 | Fire safety log book | Fire safety - Fire alarm system |  | Copies of relevant fire system inspection records as undertaken by Competent Persons |  | The Regulatory Reform (Fire Safety) Order 2005 & BS5839
12.22 |  |  | PM_80_15_31 | Fire safety log book | Fire safety - Fire smoke vents |  | Copies of relevant fire system inspection records as undertaken by Competent Persons |  | BS5720/BS5588
12.23 |  |  | PM_70_80_80 | Smoke extract and control system commissioning report | Fire safety - Fire smoke extracts |  | Copies of all relevant fire system maintenance records |  | BS5720/BS5588
12.24 |  |  | PM_70_30_30 | Fire and smoke damper test certificate | Fire safety - Fire shutters |  | Copies of all relevant fire system maintenance records |  | BS476/BS5588
12.25 |  |  | PM_70_30_79 | Smoke curtain drop test and commissioning certificate | Fire safety - Fire curtains |  | Copies of all relevant fire system maintenance records |  | BS7436/BS5588
12.26 |  |  | PM_70_75_31 | Fire alarm test certificate | Fire safety - Functional test of fire systems |  | Copies of all relevant fire system maintenance records |  | BS7436/BS5588 |  |  | Has the system cause and effect been tested to confirm operational function of smoke curtains, vents, shutters, dampers, extract, lifts escalators, pressurisation fans etc?
12.27 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire safety - Fire extinguishers |  | Copies of all relevant fire extinguishers test records |  | BS5306
12.28 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire safety - Sprinkler system testing |  | Copies of all relevant weekly sprinkler test been carried out and recorded on insurance company pro-forma |  | BS5306/LPC Rules
12.29 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire safety - Sprinkler system servicing |  | Copies of all relevant sprinkler system maintenance |  | BS5306/LPC Rules
12.3 |  |  | PM_70_30_30 | Fire and smoke damper test certificate | Fire safety - Escape route pressure test (pressurisation fans) |  | Copies of all relevant fire system maintenance records |  | BS5588
12.31 |  |  | PM_70_30_30 | Fire and smoke damper test certificate | Fire safety - Fire dampers |  | Copies of all relevant fire damper maintenance records |  | BS476/BS5588
12.32 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire safety - Hose reel |  | Copies of all relevant hose reel maintenance records |  | BS5306
12.33 |  |  | PM_70_30_27 | Fire hydrant and mains commissioning certificate | Fire safety - Dry/wet risers |  | Copies of all relevant dry/wet riser maintenance records |  | BS5306
12.34 |  |  | PM_70_75_28 | Emergency lighting test report | Fire safety - Emergency lighting (monthly) |  | Copies of all relevant emergency lighting maintenance records |  | Electricity at Work Regulations 1989 & BS5266
12.35 |  |  | PM_70_75_28 | Emergency lighting test report | Fire safety - Emergency lighting (yearly) |  | Copies of all relevant emergency lighting maintenance records |  | Electricity at Work Regulations 1989 & BS5266
12.36 |  |  | PM_80_15_31 | Fire safety log book | Fire safety - Fire log book |  | Copy of the latest UpToDate fire log book |  | BS5588
12.37 |  |  | PM_70_90_27 | Electrical systems record drawings | Electricity - Documentation |  | Copy of all relevant electrical schematic layout of electrical supply route and primary distribution complete with any amended when changes occurred |  | Electricity at Work Regulations 1989 and BS7671
12.38 |  |  | PM_70_15_27 | Electrical test certificate | Electricity - Fixed electrical testing to mobile accommodation |  | Copies of all relevant Electrical Safety Certificates and fixed electrical testing certificates |  | Electricity at Work Regulations 1989 and BS7671
12.39 |  |  | PM_70_15_27 | Electrical test certificate | Electricity - Portable appliance testing (pat) inc microwaves |  | Copies of all electrical PAT testing certificates |  | PUWER 1998 & BS 7671
12.4 |  |  | PM_70_15_76 | Secondary and backup electricity supplies test certificate | Electricity - Generators |  | Copy of all historical generator test runs and building load tests including maintenance records
12.41 |  |  | PM_70_15_76 | Secondary and backup electricity supplies test certificate | Electricity - Uninterruptable power supply (ups) |  | Copy of all relevant maintenance records
12.42 |  |  | PM_70_75_37 | High-voltage electrical installation test report | Electricity - High voltage |  | Copy of all relevant maintenance including where appropriate HV system and oil tests results. |  | Electricity at Work Regulations
12.43 |  |  | PM_30_30_96 | Water management information | Water hygiene and Legionella prevention - Plans & risk assessments |  | Copies of all relevant Water Risk Assessments undertaken. |  | ACOP L8
12.44 |  |  | PM_30_30_96 | Water management information | Water hygiene and Legionella prevention - Training |  | Copies of all written “Scheme of Control” including primary layout and isolation points |  | ACOP L8 2013
12.45 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Cooling towers – dosing regime |  | Copy of all relevant water log books maintained complete with all responsibilities defined for cleaning regime along with all water quality documentation |  | ACOP L8 2013
12.46 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Cooling towers – Water quality checks |  | Copies of the Duty Holder and Responsible Person received training |  | ACOP L8 2013
12.47 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Cooling towers – disinfection |  | Copies of any relevant water quality chemical checks and maintenance records |  | ACOP L8 2013
12.48 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Cooling towers – notification/ change of operation / confirmation |  | Copies of all documented Cooling Tower registered and logged with the Local Authority |  | The Notification of Cooling Towers and Evaporative Condensers Regulations
12.49 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Domestic water – temperature checks |  | Copies of all relevant water quality checks - water temperature records |  | ACOP L8 2013 - including records for testing of all hot water service TMVs in accordance with BS6700 and tests to comply with HSE Document L8 and HGN ‘Safe Hot Water and Surface Temperatures
12.5 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Domestic water – tank tvc legionella |  | Copies of all relevant water quality checks - water temperature records |  | ACOP L8 2013
12.51 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Domestic water – tank showers |  | Copies of all relevant water quality checks - storage tank maintenance and inspection records |  | ACOP L8 2013
12.52 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Domestic water – storage calorifiers |  | Copies of all relevant water quality checks -shower heads dismantled and cleaned and descaling records |  | ACOP L8 2013
12.53 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Domestic water – disinfection |  | Copies of all relevant water quality checks - records of water calorifiers inspections |  | ACOP L8 2013
12.54 |  |  | PM_70_15_96 | Water quality and flushing test certificate | Water hygiene and Legionella prevention - Water sampling – flushing |  | Copies of all relevant water quality checks - current test certificate |  | ACOP L8 2013
12.55 |  |  | PM_70_15_34 | Gas installation safety certificate | Gas safety tests |  | Copy of all relevant Gas Safety certificates |  | The Gas Safety (Installation and Use) Regulations 1998 & ACOP L56
12.56 |  |  | PM_70_30_45 | Kitchen equipment certificate | Kitchen equipment certificate
12.57 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems -Anchor points (eyebolt) testing |  | Copies of all inspection and tests in the last year undertaken by competent person including a full certificate of compliance without limitations. |  | BS EN 795, BS 7883
12.58 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems -Cradles, trolleys gantry and runways |  | Copies of all records of systems having been inspected and tested and fully compliant without remedial works outstanding |  | LOLER/PUWER Regs 1998, BS 6037
12.59 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems - Man safe or other roof protection |  | Copies of all records of systems having been inspected and tested and fully compliant without remedial works outstanding |  | BS7883
12.6 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems - Harness and lanyard |  | Copies of all records of systems having been inspected and tested and fully compliant without remedial works outstanding |  | PUWER
12.61 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems - Building risk assessment |  | Copies of all relevant building safety risk assessments been undertaken |  | BS7883
12.62 |  |  | PM_70_75_03 | Access equipment test report | Man safe systems - Fixed ladders |  | Copy of all project/site Ladder Registers |  | BS EN 131
12.63 |  |  | PM_70_80_45 | Kitchen ventilation certificate | Ventilation - Kitchen extracts |  | Copies of all relevant records of systems having been checked and cleaned as necessary- in accordance with SFG 20 |  | BS 6174
12.64 |  |  | PM_80_15_94 | Ventilation maintenance strategy | Ventilation - LEV system documentation |  | Copies of all relevant test and inspection records |  | BS5726 & COSHH Regs |  |  | To comply with Regulation 7 of COSHH, LEV systems should be examined and tested at least every 14 months and a suitable record kept for at least 5 years from the date on which it was made.
12.65 |  |  | PM_70_80_03 | Air conditioning systems commissioning certificate | Air Conditioning - Inspection |  | Copies of all relevant records of Air Conditioning Systems maintenance including condensate drain drains |  | Energy Performance of Buildings (Certificates and Inspections) Regulations 2008
12.66 |  |  | PM_70_80_03 | Air conditioning systems commissioning certificate | Air Conditioning - F gas documents |  | Copies of registers of all AC equipment containing more than 3 kgs of HFC refrigerant and is it up-to-date? |  | F Gas Regulations 2015
12.67 |  |  | PM_70_80_03 | Air conditioning systems commissioning certificate | Air Conditioning - F gas records |  | Copies of all records of leak checks retained for 5 years for a minimum of 5 years |  | F Gas Regulations 2015
12.68 |  |  | PM_70_75_49 | Lightning protection installation test report | Lightning protection maintenance records |  | Copies of all relevant test certificates |  | BS EN 62305:2006
12.69 |  |  | PM_70_30_29 | Fire-rated glazing and framing test certificate | Glazing – risk assessment |  | Copies of any initial survey of the building carried out to identify areas where safety glazing should be in place, and actioned |  | Workplace (Health, Safety and Welfare Regulations 1992) & Building Reg’s Part M
12.7 |  |  | PM_35_40_35 | Hazardous materials control requirements | Storage of hazardous substances |  | Copies of all relevant storage and use of hazardous substances checks and inspections |  | COSHH Regulations 2002. Consideration should be given to fuel storage tanks and the required certification
12.71 |  |  | PM_80_10_93 | Vehicle parking management plans | Car parking |  | Copies of all car parking risk assessments |  | The Workplace (Health, Safety and Welfare) Regulations 1992
12.72 |  |  |  | < add new row for each additional deliverable>